## Slide 1: Investigating a Higher Renewables Portfolio Standard In California
Power Association of California Symposium
May 20, 2014
San Francisco, CA
  Nancy E. Ryan
  Director, Policy and Strategy

## Slide 2: About the Study
Study sponsors:
  Los Angeles Dept. of Water & Power
  Southern California Edison Co.
  Pacific Gas and Electric Co.
  San Diego Gas & Electric Co.
  Sacramento Municipal Utility District
  Technical input from California ISO
Advisory panel:
  Dr. Dan Arvizu – Director and CEO of National Renewable Energy Laboratory
  Dr. Severin Borenstein – Director of the University of California Energy Institute and Co-Director of the Energy Institute at Haas School of Business, UC Berkeley
  Dr. Susan Tierney – Managing Principal at Analysis Group Inc., Boston, MA
  Mr. Stephen Wright – Retired Administrator, Bonneville Power Administration; General Manager, Chelan County Public Utility District
Analysis team: Energy + Environmental Economics (E3) with support from DNV KEMA & ECCO International
Available at: http://www.ethree.com/public_projects/renewables_portfolio_standard.php

## Slide 3: Study focus: operational challenges from high renewable penetration (40-50%)
E3’s study looks at thousands of potential operating days as renewables rise to 50%
Core question: How serious and pervasive are operating challenges as renewable penetration rises above 33%?
The CAISO duck chart illustrates operational challenges at 33% RPS
It shows just a single day in March as renewables rise to 33%

## Slide 4: With higher renewables managing Net Load will be the challenge
Sweltering Summer Day
“Dog Days”
Delightful Spring Day
“Duck Days”

## Slide 5: High Variable Renewable Penetration Stresses the Grid in New Ways
“Dog Days”
Highest Load Day
“Duck Days”
Highest Ramp Day
Historical system planning challenge: meet gross peak load on hottest days
High renewable penetration makes net peak lower and later
Need enough generating capacity
Historically an easy day to manage
Emerging system planning challenge: manage diurnal swings in net load
Need enough flexibility in the system

## Slide 6: Example Day in April under 33%, 40% and 50% RPS
Chart shows increasing overgeneration above 33%
  Overgeneration is very high on some days under the 50% Large Solar case
  Fossil generation is reduced to minimum levels needed for reliability
Renewable curtailment is a critical strategy to maintain reliability
  Reduces overgeneration
  Mitigates ramping events

## Slide 7: Overgeneration Is Extensive and Can Occur in Any Month
Average overgeneration (MW) by month-hour, 50% Large Solar Case:

## Slide 8: E3 investigated several potential solutions, most were found to be effective
Potential solutions:
  Diversified portfolio (more wind and geothermal, less solar)
  Enhanced regional coordination
  Conventional demand response (down only)
  Advanced demand response (down and up)
  Energy storage
Solutions considered individually (each @ 5000 MW)
Solutions may be combined:
  Further study needed to identify optimal combination
  Best mix of solutions depends on renewable portfolio

## Slide 9: Overgen is less severe, frequent with diverse renewable portfolio
Average Hourly Overgeneration in 2030
Diverse Renewable Portfolio
Large Solar Case
…
…

## Slide 10: Potential Integration Solution: Energy Storage Case
Assuming 5,000 MW of diurnal energy storage in CA reduces overgeneration from 9% in the 50% RPS Large Solar case to 4% of total renewable energy.
Storage charges during the day & discharges at night.
Example April day

## Slide 11: Potential Integration Solution: Enhanced Regional Coordination Case
Increasing California’s export capability by 5,000 MW (6,500 MW total) reduces overgeneration from 9% in the 50% RPS Large Solar case to 3% of total renewable energy
Example April day

## Slide 12: Potential Integration Solution: Advanced Demand Response
Advanced DR can adjust load down and up
Conventional DR (downward only) does not help
Smart charging of EVs is a form of Advanced DR: cars charge during day at work and late at night at home

## Slide 13: Change in Average Rates of Flexibility Solution Cases Relative to 33% RPS (2012 cents/kWh)
5,000 MW of flexibility solutions reduce the cost of meeting a 50% RPS in 2030, but result in higher average rates compared to the 33% RPS scenario

## Slide 14: Insufficient downward flexibility of the system causes curtailment
Conventional fleet performance and flexibility Representative day with the largest net load ramp
50% RPS Large Solar Case, no flexibility solutions implemented
Ramping capability always exceeds ramping need
Curtailment occurs because the system cannot ramp down low enough

## Slide 15: Potential Next Steps to Accommodate Higher Renewables
Increase regional coordination
  Allows sharing of flexible resources across West to support renewable integration
Pursue a diverse portfolio of renewable resources
Implement a long-term, sustainable solution to address overgeneration before the issue becomes more challenging
Implement distributed generation solutions
  Sustainable, cost-based procurement strategy; reexamination of retail rate design & net energy metering policy; distribution-level solutions and upgrades, including smart inverters with low-voltage ride-through capabilities that allow distributed PV to operate under grid faults

## Slide 16: Thank You!
Full Author List:
Arne Olson, E3
(arne@ethree.com)
Amber Mahone, E3
(amber@ethree.com)
Dr. Elaine Hart, E3
(elaine.hart@ethree.com)
Dr. Jeremy Hargreaves, E3
Ryan Jones, E3
Energy and Environmental Economics, Inc. (E3) 101 Montgomery Street, Suite 1600 San Francisco, CA 94104 Tel 415-391-5100 Web http://www.ethree.com
Gabriel Kwok, E3
Nicolai Schlag, E3
Dr. Nancy Ryan, E3
Rod Frowd, ECCO
Dave Korinek, DNV KEMA
Dr. Ren Orans, E3