## Slide 1: Biological Aspects of OTC Compliance in California
October 15, 2013
John Steinbeck
Tenera Environmental
San Luis Obispo, CA
jsteinbeck@tenera.com

## Slide 2: CA OTC Policy Two Options for Compliance
Track 1 – Reduce intake flow to levels achievable using wet-closed cycle cooling (93% flow reduction) and reduce through screen velocity to less than 0.5 fps
Track 2 – Reduce impingement mortality and entrainment (IM&E) to a level comparable (90%) to Track 1 using operational and/or structural controls
  Must demonstrate Track 1 not feasible (can’t use cost)
  Verification monitoring must demonstrate a 84% (90% of 93%) reduction in IM&E relative to design flow
  If compliance based solely on flow the reductions must be compared on a monthly basis using actual average 2000-2005 flows
  Monitoring required to verify 0.5 fps screen velocity

## Slide 3: CA OTC Policy
For all plants: Measures must be implemented to mitigate the interim impingement and entrainment impacts resulting from the cooling water intake structure(s), commencing October 1, 2015 and continuing until final compliance.
Also, 36 months IM&E monitoring required for plants pursuing compliance under Track 2

## Slide 4: Achieving Compliance
Compliance will require strategy that integrates technology and operational measures and maximizes biological data on entrainment
  Species and sizes of fish larvae being entrained will affect choice of compliance technology
  Seasonal and diel patterns of abundance affect options for operational adjustments of flow and decision for use of VSDs

## Slide 5: Achieving Compliance
Data collected from the large number of studies in CA over the past decade will help inform compliance decisions
  composition, size distribution, and morphology of fish larvae subject to entrainment
  seasonal and diel patterns of larval abundance

## Slide 6: Estimating Screen Effectiveness
body shapes vary among species
species composition varies across facilities
CIQ goby
white croaker

## Slide 7: Estimating Screen Effectiveness
Data on lengths and corresponding head capsule dimensions of larvae from numerous studies in CA used to estimate effectiveness of screens at reducing mortality
available at www.waterboards.ca.gov

## Slide 8: Estimating Screen Effectiveness
Parameters from relationship of length and head capsule dimensions used to predict probability of entrainment for various length larvae
 | Square Mesh Opening |  |  | 
Length (mm) | 0.5 mm | 0.75 mm | 1.0 mm | 2.0 mm
1 | 1 (0) | 1 (0) | 1 (0) | 1 (0)
2 | 1 (0) | 1 (0) | 1 (0) | 1 (0)
3 | 1.000 (0.001) | 1 (0) | 1 (0) | 1 (0)
4 | 0.586 (0.308) | 1 (0) | 1 (0) | 1 (0)
5 | 0.011 (0.019) | 0.976 (0.034) | 1 (0) | 1 (0)
6 | 0 (0) | 0.481 (0.246) | 0.999 (0.001) | 1 (0)
7 | 0 (0) | 0.024 (0.028) | 0.894 (0.091) | 1 (0)
8 | 0 (0) | 0.000 (0.000) | 0.359 (0.175) | 1 (0)
9 | 0 (0) | 0 (0) | 0.030 (0.027) | 1 (0)
10 | 0 (0) | 0 (0) | 0.001 (0.001) | 1 (0)
11 | 0 (0) | 0 (0) | 0 (0) | 1.000 (0.000)
12 | 0 (0) | 0 (0) | 0 (0) | 0.993 (0.005)
13 | 0 (0) | 0 (0) | 0 (0) | 0.935 (0.035)
14 | 0 (0) | 0 (0) | 0 (0) | 0.722 (0.087)
15 | 0 (0) | 0 (0) | 0 (0) | 0.398 (0.093)
16 | 0 (0) | 0 (0) | 0 (0) | 0.141 (0.050)
17 | 0 (0) | 0 (0) | 0 (0) | 0.035 (0.016)
18 | 0 (0) | 0 (0) | 0 (0) | 0.005 (0.003)
19 | 0 (0) | 0 (0) | 0 (0) | 0.001 (0.000)
20 | 0 (0) | 0 (0) | 0 (0) | 0.000 (0.000)

## Slide 9: Estimating Screen Effectiveness
Studies have also provided extensive data on lengths of larvae susceptible to entrainment – not achievable from one study without very frequent sampling.
Need to account for protection of larger larvae.

## Slide 10: Operational Controls
Chart: 
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Day | 24496172 | 26499314 | 27190344 | 20535816 | 23426009 | 16774411 | 8703866 | 10039656 | 4607439 | 9548269 | 9810552 | 13925586
Night | 20489184 | 34848088 | 23440221 | 40277293 | 64570667 | 30070109 | 15516614 | 18087783 | 17870506 | 33513427 | 12831945 | 9126102
Patterns of seasonal and diel variation in larval abundance allow for implementation of operation controls that provide large reductions in entrainment

## Slide 11: Operational Controls
We have worked with clients to develop a modeling tool that estimates levels of entrainment reductions provided by varying plant flow by month, hour, or on a diel basis.
Data from three-year monitoring will be useful in verifying that operational controls are providing the necessary entrainment reductions for compliance.

## Slide 12: Summary
John Steinbeck
Tenera Environmental
jsteinbeck@tenera.com
805-541-0310
New and existing biological data on IM&E will be critical in developing a compliance strategy
Questions?